PART 1 General

1.1	SYSTEM DESCRIPTION

1.1.1  Provide MDL Low Surface Temperature (LST) Floor Mount units where perimeter heating is shown as represented by Christopher Makarewicz of MDL Solutions @ 289 799-3414 chris@mdlsoln.com.  Alternates Shall not be accepted.

- 1.1.2  LST hydronic heating device wall mounted  shall be robust in design and provide suitable for public facility areas.

1.1.3	The water source heating equipment shall be certified for outputs based on EN442 standards

1.2 	QUALITY ASSURANCE

1.2.1  Each Units shall be fully tested at the factory.

1.2.2  All aluminum components shall be certified to meet ASTM G53 UV-resistance

1.2.3  Surface temperature remains safe at all times based on DHSS DN 4 1992 regulation and subsequent revision.

1.2.4 All units shall be individually packaged and labeled for eased on site locating and installation

PART 2 Mechanical Parts

2.1 Cabinets

- 2.1.1  The Cabinet shall be fabricated with 16 gauge electrolytic galvanized steel and will be coated expoy polyester baked at 392°F. Available in one colour as standard White.

- 2.1.2  The Top grille shall provide supply air and bottom opening shall provide return.

- 2.1.3  The Cabinet front face shall be constructed of a single uniform piece seamless in construction.

- 2.1.4  The Cabinet shall be fabricated with heat exchanger support bracket.  Standard configuration will be center mounted.

2.1.5  All Valve connections shall be internal to the unit cabinet valve compartment as provided inside of the cabinet unless separate enclosures are supplied.

2.1.6  The Cabinet shall be fabricated such that there are no exposed corners or gaps.  All corners shall be joined to form one solid piece – gaps are not permitted.

- 2.1.7  The unit shall come with locate and fasten support structure.

- 2.1.8   The Cabinet shall be factory Parts Warranted for 10 Years

2.1.9 OPTIONAL Any Colour cabinet

2.1.10 OPTIONAL Any Wood Pattern finish

2.1.11 OPTIONAL any image licensed to the final owner may be used

2.1.12 OPTIONAL Supply air grille to be selected from Catalogued standards.

2.2 Heat Exchanger

2.2.1  The Heat exchanger shall be of copper and aluminum construction.  Shall be composed of round, seamless circulation tubes type L Copper, and two brass collectors.

2.2.2 The Fins shall be connected to the heat exchanger by expansion method only.

2.2.3  The Heat exchanger shall be factory pressure tested to 300 PSI

2.2.4  The Heat exchanger shall be easily removable from cabinet if required.

2.2.5  The Heat exchanger shall be coated with dirt repellent and dust proof lacquer in graphite grey  with 70% gloss to match cabinet.

2.2.6 The Heat exchanger shall be standard same end supply/ return.  Opposite end heat exchangers shall be optionally accepted.

2.2.7  The Heat exchanger shall have ASTM G53 certification.

2.2.8  Each individual heat exchanger shall have EN442 certification.  Output Correction factors will not be considered equivalent to establish output capacities.

2.2.9  Each Heat exchanger shall be of ultra low thermal inertia in design.

2.2.10  Each Heat exchanger shall come with 1/8”air vents.

2.2.11 The Heat Exchanger fins shall be corrugated by design.

- 2.2.12  The Heat Exchanger shall be factory Parts Warranted for 10 Years

2.3  VALVES AND CONTROLS

2.3.1  The valve shall have a specifically shortened thermostatic valve in order to be fully concealed within the casing.

2.3.2 The valve shall be suitable for One or Two Pipe systems

2.3.3 The connection to the floor or wall must be specified before ordering

2.3.4  The valve shall have as standard operation duty of shutoff/ Balancing and zone control.

2.3.5  The valve shall come with 0-10V actuator at 24VDC power requirements OR manual TRV.

2.3.6  Two pipe continuous adjustable between (0.132 to 2.642) UsGPM.

2.3.7  Single pipe 9.07 UsGPM diverting capability with 35% flow through unit.

PART   3  - EXECUTION

  - INSTALLATION

    - Maintain factory installed pipe caps until water connections are made.

    - Install units in accordance with manufacturer’s instructions and install all accessories specified herein.

    - Locate units according to the drawings and ensure that mounting position allows full access to the service panels, filters, etc.

    - In order to totally block off the cold draughts from the window it shall be preferable that the fin tube element covers the full length of the window.

END OF SECTION